## Report (hidden)
|  | WATER COOLED CHILLERS AND LOW TEMP BOILERS |  |  |  |  | WW210
UNIT PERFORMANCE DATA
WW SERIES
|  | FHP MANUFACTURING HIGH-EFFICIENCY WATER SOURCE HEAT PUMPS |  |  |  |  | Refrigerant R-410A
2
Electrical Specifications
Voltage |  | Voltage | Stages | Compressor |  |  | Unit
Code |  |  |  | RLA |  | LRA | MCA | MFS
-3 |  | 208-230/3/60 | 1 | 59.1 |  | 425 | 73.9 | 130
-4 |  | 460/3/60 | 1 | 26.4 |  | 187 | 33 | 50
-5 |  | 575/3/60 | 1 | 26 |  | 148 | 32.5 | 50
| Chiller Performance |  |  |  | Heating Performance
Condenser |  | Condenser Entering Fluid Temp. (F) | 85 | Source |  |  | Source Entering Fluid Temp. (F) | 70
|  | Leaving Fluid Temp. (F) | 95.5153 |  |  |  | Leaving Fluid Temp. (F) | 58.6175
|  | Flow Rate (GPM) | 40 |  |  |  | Flow Rate (GPM) | 40
|  | Pressure Drop (FOH) | 11.8318 |  |  |  | Pressure Drop (FOH) | 12.865
|  | % Propylene Glycol | 0 |  |  |  | % Propylene Glycol | 0
|  | Freeze Point | 32 |  |  |  | Freeze Point | 32
Evaporator |  | Evaporator Entering Fluid Temp (F) | 55 | Load |  |  | Load Entering Fluid Temp. (F) | 70
|  | Leaving Fluid Temp. (F) | 44.4286 |  |  |  | Leaving Fluid Temp. (F) | 86.6113
|  | Flow Rate (GPM) | 32 |  |  |  | Flow Rate (GPM) | 32
|  | Pressure Drop (FOH) | 9.0483 |  |  |  | Pressure Drop (FOH) | 8.2223
|  | % Propylene Glycol | 0 |  |  |  | % Propylene Glycol | 0
|  | Freeze Point | 32 |  |  |  | Freeze Point | 32
|  | Chiller Capacity (BtuH) | 169142.9359 |  |  |  | Heating Capacity (BtuH) | 265780.115
|  | Input Watts (W) | 12063.9501 |  |  |  | Input Watts (W) | 11175.0336
|  | EER (BtuH/W) | 14.0205 |  |  |  | COP (W/W) | 6.9705
|  | Heat of Rejection (BtuH) | 210305.1337 |  |  |  | Heat of Absorbtion (BtuH) | 227650.9004
Warnings:
Units are complete packages featuring 1 stage operation and containing refrigeration compressor, reversing valve, expansion valve metering device and coaxial style water to refrigerant heat exchangers. Also included are safety controls: overload protection for compressor, high and low refrigerant pressure switches and lock-out control circuit (CAP 4.05). |  |  |  |  | FHP Manufacturing
601 N.W. 65th Court Fort Lauderdale, FL 33309
Phone: (954) 776-5471 Fax: (800) 776-5529
http://www.fhp-mfg.com
As a result of continued research and development, all ratings are subject to change without notice | [7 empty] | 2026-07-28
Units are complete packages featuring 1 stage operation and containing refrigeration compressor, expansion valve metering device and double wall coaxial style water to refrigerant heat exchanger on load side. Also included are safety controls: overload protection for compressor, high and low refrigerant pressure switches and lock-out control circuit (CAP 4.05).
Units are complete packages featuring 1 stage operation and containing refrigeration compressor, reversing valve, expansion valve metering device and coaxial style water to refrigerant heat exchangers. Also included are safety controls: overload protection for compressor, high and low refrigerant pressure switches and lock-out control circuit (CAP 4.05).
Units are complete packages featuring 2 stage operation and containing refrigeration compressors, reversing valves, expansion valve metering devices and coaxial style water to refrigerant heat exchangers. Also included are safety controls: overload protection for compressors, high and low refrigerant pressure switches and lock-out control circuit (CAP 4.05).

## Disclaimer (hidden)
Chiller Application Data Program v4.05
© 2007, FHP Manufacturing
Only original, unaltered copies of this file obtained directly from FHP Manufacturing are guaranteed to be virus free. If there is any question of the source of this file, contact FHP Manufacturing for an original copy. FHP Manufacturing does not guaranty, nor is liable for software compatibility or lack thereof with the user's hardware or software. FHP Manufacturing assumes no liability for any hardware or software problems or loss of data that may arise from use of this program.
Although this program has been designed to provide the most accurate performance data possible, FHP Manufacturing does not guaranty nor certify that the results obtained from this program will match actual equipment performance.
All product specifications are subject to change without notice.
Return to Program

## Performance
FHP Manufacturing Chiller Application Data |  |  |  | Version 4.05
WP120
General Entering Conditions | Cooling |  |  | Heating
Source Water Flow (GPM) | 40 |  | Source Water Flow (GPM) | 40
Load Water Flow (GPM) | 32 |  | Load Water Flow (GPM) | 32
Source Entering Water Temp (F) | 85 |  | Source Entering Water Temp (F) | 70
Load Entering Water Temp (F) | 55 |  | Load Entering Water Temp (F) | 70
Source Percent Propylene Glycol | 0 |  | Source Percent Propylene Glycol | 0
Load Percent Propylene Glycol | 0 |  | Load Percent Propylene Glycol | 0
Unit Performance | Cooling |  |  | Heating
Source Pressure Drop (FOH) | 11.8318 |  | Source Pressure Drop (FOH) | 12.865
Load Pressure Drop (FOH) | 9.0483 |  | Load Pressure Drop (FOH) | 8.2223
Cooling Capacity (BtuH) | 169142.9359 |  | Heating Capacity (BtuH) | 265780.115
Heat of Rejection (BtuH) | 210305.1337 |  | Heat of Absorbtion (BtuH) | 227650.9004
Power Input (W) | 12063.9501 |  | Power Input (W) | 11175.0336
EER | 14.0205 |  | COP | 6.9705
Source Leaving Water Temp (F) | 95.5153 | 95.5153 | Source Leaving Water Temp (F) | 58.6175 | 58.6175
Load Leaving Water Temp (F) | 44.4286 | 44.4286 | Load Leaving Water Temp (F) | 86.6113 | 86.6113
Head Pressure (PSIG) | 337.5653 | 104.5356 | Head Pressure (PSIG) | 288.8812 | 93.6714
Suction Pressure (PSIG) | 100.9571 | 32.0623 | Suction Pressure (PSIG) | 127.9138 | 44.2289
Source Freeze Point | 32 |  | Source Freeze Point | 32
Load Freeze Point | 32 |  | Load Freeze Point | 32
Note on C23: RED - Source leaving water temperature is approaching limits of unit.
Note on C24: BLUE - Antifreeze is required for load water.
Note on C26: BLUE - Head pressure is too low for reliable operation. RED - Head pressure is too high for reliable operation.
Note on C27: BLUE - Suction pressure is too low for reliable operation. RED - Suction pressure is too high for reliable operation.
Note on F23: BLUE - Antifreeze is required for source water.
Note on F24: RED - Load leaving water temperature approaching limits of unit.
Note on F26: BLUE - Head pressure is too low for reliable operation. RED - Head pressure is too high for reliable operation.
Note on F27: BLUE - Suction pressure is too low for reliable operation. RED - Suction pressure is too high for reliable operation.
Default Conditions
Print Report
Fit View to Screen
Inch-Pound Units
SI Units
Disclaimer
Print Submittal

## Calc (hidden)
9 |  |  | Rev: 1-07 |  |  | Units | E | Refrig. | 2
Modelling Constants
Selected Model |  | WW210 |  |  |  | Drawing | 2 |  | Refrigerant R-410A
Compressor Coefficients
| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
c | 146844.7802 | 2530.0897 | -725.6045 | 28.1275 | -0.55501 | 1.8584 | 0.09198 | -0.11264 | -0.043758 | -0.0076663
w | 5909.2372 | 159.8744 | -43.501 | 2.2867 | -3.8022 | 1.1543 | 0.014723 | -0.029084 | 0.022894 | -0.0019807
a
m
Heat Exchanger Coefficients
Condensing Temp |  |  |  | Evaporating Temp |  |  | Rated Conditions
Evap | 0.05 |  |  | Evap | 0.85 |  | Cooling |  | Heating
Cond | 0.97 |  |  | Cond | 0.02 |  | SGPM | 40 | SGPM | 32
Approach | 14.5 |  |  | Approach | 12 |  | LGPM | 32 | LGPM | 40
[7 empty] | SEWT | 85 | SEWT | 70
Pressure Drop |  | 0.0165 |  | Max GPM | 50 |  | LEWT | 55 | LEWT | 70
Cooling Glycol Formulas
Performance Modifiers |  |  | Iteration #0 Modifiers |  |  |  | Source% | 0 | Load% | 0
Capacity | 1.017 |  | LST(clg) | 400 | LST(htg) | 325 | P.D. Mod | 0.93725 | P.D. Mod | 1.0711
Watts | 1.02 |  | LLT(clg) | 325 | LLT(htg) | 400 | H.T. Coeff | 500 | H.T. Coeff | 500
[7 empty] | Bulk ST | 90.2576 | Bulk LT | 49.7143
Nameplate Data | [6 empty] | Heating Glycol Formulas
Volt Code | Voltage | RLA | LRA | MCA | MFS |  | Source% | 0 | Load% | 0
-3 | 208-230/3/60 | 59.1 | 425 | 73.9 | 130 |  | P.D. Mod | 1.0191 | P.D. Mod | 0.97328
-4 | 460/3/60 | 26.4 | 187 | 33 | 50 |  | H.T. Coeff | 500 | H.T. Coeff | 500
-5 | 575/3/60 | 26 | 148 | 32.5 | 50 |  | Bulk ST | 64.3087 | Bulk LT | 78.3056
Calculations
Cooling Mode | [10 empty] | Error Check
EST | 85 |  | IT#0 LST | 95 |  | Delta P (S) | 11.8318 |  | Antifreeze? |  | Code
SGPM | 40 |  | IT#0 LLT | 44.8438 |  | Delta P (L) | 9.0483 |  | N |  | 0 | 1
ELT | 55 |  |  |  |  | Head | 337.5653 | SFP | 32 |  | 0 | 2
LGPM | 32 |  |  |  |  | Suction | 100.9571 | LFP | 32 |  | 0 | 3
[11 empty] | 0 | 4
Iteration # | Cond T. | Evap T. | CCap | Watts | HCap | EER | COP | LST | LLT |  | 0 | 5
1 | 104.2961 | 32.2336 | 169970.9312 | 12032.8994 | 211027.1839 | 14.1255 | 5.14 | 95.5514 | 44.3768 |  | 0 | 6
2 | 104.5518 | 32.0407 | 169052.9003 | 12065.9665 | 210221.9781 | 14.0107 | 5.1063 | 95.5111 | 44.4342 |  | 0 | 7
3 | 104.5337 | 32.0646 | 169152.6906 | 12063.719 | 210314.0997 | 14.0216 | 5.1095 | 95.5157 | 44.428 |  | 0 | 8
4 | 104.5358 | 32.062 | 169141.734 | 12063.9785 | 210304.0285 | 14.0204 | 5.1091 | 95.5152 | 44.4286 | LLT-FP | 0 | 9
5 | 104.5356 | 32.0623 | 169142.9359 | 12063.9501 | 210305.1337 | 14.0205 | 5.1092 | 95.5153 | 44.4286 | 12.4286 | 0 | 10
[11 empty] | 0 | 11
Heating Mode | [10 empty] | 0 | Agregate Code
EST | 70 |  | IT#0 LST | 61.875 |  | Delta P (S) | 12.865 |  | Antifreeze? |  | Code
SGPM | 40 |  | IT#0 LLT | 82.5 |  | Delta P (L) | 8.2223 |  | N |  | 0 | 1
ELT | 70 |  |  |  |  | Head | 288.8812 | SFP | 32 |  | 0 | 2
LGPM | 32 |  |  |  |  | Suction | 127.9138 | LFP | 32 |  | 0 | 3
[11 empty] | 0 | 4
Iteration # | Cond T. | Evap T. | CCap | Watts | HCap | EER | COP | LLT | LST |  | 0 | 5
1 | 91.7594 | 45.5719 | 235775.3367 | 11094.9179 | 273631.1967 | 21.2508 | 7.2282 | 87.1019 | 58.2112 |  | 0 | 6
2 | 93.8997 | 44.0608 | 226660.8538 | 11186.1312 | 264827.9336 | 20.2627 | 6.9386 | 86.5517 | 58.667 |  | 0 | 7
3 | 93.6443 | 44.249 | 227769.3532 | 11173.7465 | 265894.1761 | 20.3843 | 6.9743 | 86.6184 | 58.6115 |  | 0 | 8
4 | 93.6752 | 44.2261 | 227634.4911 | 11175.2128 | 265764.317 | 20.3696 | 6.97 | 86.6103 | 58.6183 | LST-FP | 0 | 9
5 | 93.6714 | 44.2289 | 227650.9004 | 11175.0336 | 265780.115 | 20.3714 | 6.9705 | 86.6113 | 58.6175 | 26.6175 | 0 | 10
[11 empty] | 0 | 11
[11 empty] | 0 | Agregate Code

## Data (hidden)
Sort | Unit | Compressor Capacity Coefficients | [9 empty] | Compressor Watt Coefficients | [9 empty] | Condensing Temp Constants |  |  | Evaporating Temp Constants |  |  | Performance Modifiers |  | Delta P | Iteration 0 Values |  |  |  | Rated Flow | [20 empty] | Cooling |  | Heating
Key | Model | c0 | c1 | c2 | c3 | c4 | c5 | c6 | c7 | c8 | c9 | w0 | w1 | w2 | w3 | w4 | w5 | w6 | w7 | w8 | w9 | Evap | Cond | Approach | Evap | Cond | Approach | Capacity | Watts | Constant | LST (Clg) | LLT (Clg) | LST (Htg) | LLT (Clg) | Load | Source | Circuits | V-Code | Voltage | RLA | LRA | MCA | MFS | V-Code | Voltage | RLA | LRA | MCA | MFS | V-Code | Voltage | RLA | LRA | MCA | MFS | EST | ELT | EST | ELT | Refrigerant |  | Drawing | Max Flow
1 | WH018 | 10718.55 | 192.844 | -62.7492 | 2.3172 | -0.43705 | 0.18705 | 0.00025428 | -0.0055788 | -0.0012853 | -0.00041553 | 0.49687 | 2.0177 | 8.5149 | 0.040172 | -0.032206 | -0.015611 | 4.2166e-06 | -0.00047508 | 0.00053781 | 4.9305e-05 | 0.09 | 0.82 | 28 | 0.67 | 0.0235 | 8 | 1 | 1.03 | 1.252 | 30 | 25 | 25 | 30 | 2.5 | 2.5 | 1 | "-0" | 115/1/60 | 16.2 | 62 | 20.3 | 35 | -1 | 208-230/1/60 | 7.6 | 33 | 9.5 | 15 | -2 | 265/1/60 | 6.9 | 26 | 8.6 | 15 | 100 | 32 | 32 | 100 | Refrigerant R-22 |  | 1 | 7
2 | WP036 | 23965.8219 | 713.4322 | 6.9326 | 10.083 | -2.9044 | -1.6295 | 0.026239 | -0.057816 | 0.0073013 | 0.0042432 | 84.797 | -15.3868 | 32.0622 | -0.2643 | 0.37547 | -0.16129 | -0.0018352 | 0.0010452 | 0.0008286 | -3.16e-05 | 0.05 | 0.98 | 14 | 0.8 | 0.055 | 12 | 1 | 1 | 0.174 | 100 | 75 | 75 | 100 | 6.6 | 8.3 | 1 | -1 | 208-230/1/60 | 18.9 | 96 | 23.6 | 40 | -3 | 208-230/3/60 | 12.2 | 75 | 15.3 | 25 | -4 | 460/3/60 | 6.2 | 40 | 7.8 | 15 | 85 | 55 | 70 | 70 | Refrigerant R-22 |  | 1 | 12
3 | WP060 | 31585.8457 | 999.4631 | -70.3448 | 6.618 | -4.1647 | 0.17495 | 0.0020182 | -0.00063319 | 0.002729 | -0.0037251 | -346.0971 | -42.4987 | 65.8971 | -0.17245 | 1.017 | -0.68243 | 0.00072823 | 0.0016517 | -0.0062009 | 0.0039271 | 0.05 | 0.923 | 21.5 | 0.8 | 0.09 | 14.5 | 1 | 1 | 0.08828 | 175 | 150 | 150 | 175 | 9.7 | 12.2 | 1 | -1 | 208-230/1/60 | 25.1 | 169 | 31.4 | 50 | -3 | 208-230/3/60 | 17.7 | 123 | 22.1 | 40 | -4 | 460/3/60 | 8.1 | 49.5 | 10.1 | 15 | 85 | 55 | 70 | 70 | Refrigerant R-22 |  | 1 | 17
4 | WP072 | 44964.4609 | 1008.9749 | -291.0977 | 10.5461 | -5.5571 | 2.5587 | 0.041541 | -0.06739 | 0.029924 | -0.014755 | -471.2022 | 22.3814 | 55.9505 | -0.13902 | -0.24616 | -0.37496 | -0.0010184 | 0.00277 | -0.00046268 | 0.0023915 | 0.05 | 0.941 | 18.3 | 0.8 | 0.04 | 11 | 1.05 | 1.05 | 0.07828 | 250 | 200 | 200 | 250 | 11 | 13.7 | 1 | -1 | 208-230/1/60 | 28.8 | 169 | 36 | 60 | -3 | 208-230/3/60 | 19.1 | 137 | 23.9 | 40 | -4 | 460/3/60 | 9.1 | 62 | 11.4 | 20 | 85 | 55 | 70 | 70 | Refrigerant R-22 |  | 1 | 17
5 | WP120 | 79399.2344 | 2024.6992 | -164.3869 | 19.6291 | -7.8377 | 0.06794 | 0.01885 | -0.070529 | 0.017401 | -0.0064571 | 3636.957 | 12.9199 | 9.3557 | 0.053215 | 0.080125 | 0.13823 | 0.0042319 | -0.0026275 | -0.00064317 | 0.0015689 | 0.05 | 0.97 | 15 | 0.82 | 0.04 | 14.5 | 1.021 | 1 | 0.0277 | 350 | 300 | 300 | 350 | 22 | 28 | 1 | -3 | 208-230/3/60 | 37.8 | 239 | 47.3 | 80 | -4 | 460/3/60 | 17.2 | 125 | 21.5 | 35 | -5 | 575/3/60 | 12.4 | 80 | 15.5 | 25 | 85 | 55 | 70 | 70 | Refrigerant R-22 |  | 2 | 35
6 | WP180 | 156180.0156 | 1957.863 | -1822.307 | 13.2534 | 7.513 | 12.615 | 0.080919 | 0.036638 | -0.12247 | -0.027729 | 874.1985 | 65.2667 | 94.2472 | 0.84548 | -1.3671 | -0.38121 | 0.0018889 | -0.0099139 | 0.0084717 | 0.0028349 | 0.05 | 0.97 | 14 | 0.8 | 0.04 | 12 | 1 | 1 | 0.0165 | 450 | 400 | 400 | 450 | 27 | 34 | 1 | -3 | 208-230/3/60 | 41 | 350 | 51.3 | 90 | -4 | 460/3/60 | 21.8 | 158 | 27.3 | 45 | -5 | 575/3/60 | 17.3 | 125 | 21.6 | 35 | 85 | 55 | 70 | 70 | Refrigerant R-22 |  | 2 | 50
7 | WP210 | 63174.2086 | 3329.1415 | 980.3453 | 29.329 | -17.6023 | -9.3157 | 0.12207 | -0.15759 | 0.060993 | 0.013413 | 899.9806 | 58.3998 | 105.167 | 0.82877 | -1.5631 | -0.20304 | 0.0073318 | -0.015667 | 0.011909 | 0.0018891 | 0.05 | 0.97 | 15 | 0.85 | 0.02 | 14.5 | 1.0174 | 1.0391 | 0.0165 | 400 | 325 | 325 | 400 | 32 | 40 | 1 | -3 | 208-230/3/60 | 48.1 | 425 | 60.1 | 100 | -4 | 460/3/60 | 23.8 | 187 | 29.6 | 50 | -5 | 575/3/60 | 21.8 | 148 | 27.3 | 45 | 85 | 55 | 70 | 70 | Refrigerant R-22 |  | 2 | 50
8 | WP240 | 79399.2344 | 2024.6992 | -164.3869 | 19.6291 | -7.8377 | 0.06794 | 0.01885 | -0.070529 | 0.017401 | -0.0064571 | 3636.957 | 12.9199 | 9.3557 | 0.053215 | 0.080125 | 0.13823 | 0.0042319 | -0.0026275 | -0.00064317 | 0.0015689 | 0.05 | 0.97 | 15 | 0.82 | 0.04 | 14.5 | 2.042 | 2 | 0.007955 | 700 | 600 | 600 | 700 | 44 | 56 | 2 | -3 | 208-230/3/60 | 37.8 | 239 | 85.1 | 110 | -4 | 460/3/60 | 17.3 | 125 | 38.7 | 50 | -5 | 575/3/60 | 12.4 | 80 | 27.9 | 40 | 85 | 55 | 70 | 70 | Refrigerant R-22 |  | 2 | 72
9 | WP360 | 156180.0156 | 1957.863 | -1822.307 | 13.2534 | 7.513 | 12.615 | 0.080919 | 0.036638 | -0.12247 | -0.027729 | 874.1985 | 65.2667 | 94.2472 | 0.84548 | -1.3671 | -0.38121 | 0.0018889 | -0.0099139 | 0.0084717 | 0.0028349 | 0.05 | 0.97 | 14 | 0.8 | 0.04 | 12 | 2 | 2 | 0.004738 | 900 | 800 | 800 | 900 | 54 | 68 | 2 | -3 | 208-230/3/60 | 41 | 350 | 92.3 | 125 | -4 | 460/3/60 | 23.7 | 158 | 49.1 | 70 | -5 | 575/3/60 | 17.3 | 125 | 38.9 | 50 | 85 | 55 | 70 | 70 | Refrigerant R-22 |  | 2 | 90
10 | WP420 | 63174.2086 | 3329.1415 | 980.3453 | 29.329 | -17.6023 | -9.3157 | 0.12207 | -0.15759 | 0.060993 | 0.013413 | 899.9806 | 58.3998 | 105.167 | 0.82877 | -1.5631 | -0.20304 | 0.0073318 | -0.015667 | 0.011909 | 0.0018891 | 0.05 | 0.97 | 15 | 0.85 | 0.02 | 14.5 | 2.0348 | 2.0782 | 0.004738 | 800 | 650 | 650 | 800 | 64 | 80 | 2 | -3 | 208-230/3/60 | 48.1 | 425 | 108.2 | 150 | -4 | 460/3/60 | 23.8 | 187 | 53.3 | 70 | -5 | 575/3/60 | 21.8 | 148 | 49.1 | 70 | 85 | 55 | 70 | 70 | Refrigerant R-22 |  | 2 | 90
11
12 | WW024 | 14963.9639 | 324.799 | 32.3902 | 3.47 | 0.80192 | -1.0738 | 0.0080317 | -0.0062237 | -0.013859 | 0.0034513 | -962.2907 | -1.0012 | 48.6434 | 0.09544 | -0.086653 | -0.36396 | 0.0015494 | -0.0024703 | 0.0012234 | 0.0014217 | 0.05 | 0.99 | 12.8 | 0.8 | 0.08 | 8 | 0.96 | 1.05 | 0.174 | 100 | 75 | 75 | 100 | 5 | 6.2 | 1 | -1 | 208-230/1/60 | 13.5 | 61 | 16.9 | 30 | -3 | 208-230/3/60 | 8.3 | 63 | 10.4 | 15 | -4 | 460/3/60 | 5 | 27 | 6.3 | 15 | 85 | 55 | 70 | 70 | Refrigerant R-410A |  | 1 | 10
13 | WW036 | 20434.3789 | 408.4368 | -103.2717 | 4.6543 | -0.96454 | 0.46079 | 0.012 | -0.018883 | -0.0018459 | -0.0027202 | -427.9745 | -14.2724 | 41.4046 | -0.115 | 0.31743 | -0.37711 | 0.0007 | 0.000465 | -0.0017833 | 0.0019242 | 0.05 | 0.98 | 12.4 | 0.8 | 0.055 | 10 | 1.02 | 1 | 0.174 | 100 | 75 | 75 | 100 | 5.3 | 6.6 | 1 | -1 | 208-230/1/60 | 14.8 | 72.5 | 18.5 | 30 | -3 | 208-230/3/60 | 9.9 | 35 | 12.4 | 20 | -4 | 460/3/60 | 4.5 | 31 | 5.7 | 15 | 85 | 55 | 70 | 70 | Refrigerant R-410A |  | 1 | 12
14 | WW048 | 25244.5977 | 613.9734 | 45.4917 | 6.5826 | -0.7653 | -1.2072 | 0.015862 | -0.024127 | -0.0068058 | 0.0017693 | -1371.0541 | -31.1564 | 85.6462 | -0.37677 | 0.72406 | -0.80042 | -0.0013903 | 0.0040539 | -0.0044038 | 0.0036982 | 0.05 | 0.941 | 17.6 | 0.8 | 0.04 | 10.8 | 1.04 | 1.01 | 0.11643 | 175 | 125 | 125 | 175 | 8.1 | 10.1 | 1 | -1 | 208-230/1/60 | 20.6 | 109 | 25.8 | 45 | -3 | 208-230/3/60 | 14.1 | 91 | 17.7 | 30 | -4 | 460/3/60 | 7.1 | 46 | 8.9 | 15 | 85 | 55 | 70 | 70 | Refrigerant R-410A |  | 1 | 17
15 | WW060 | 36005.2461 | 907.9749 | -18.4169 | 9.6422 | -2.1577 | -0.99203 | 0.04578 | -0.06338 | 0.0017438 | 0.000452 | -2319.134 | -7.4615 | 112.0605 | -0.09131 | 0.11179 | -0.8882 | 0.0017189 | -0.000738 | -0.000364 | 0.0037419 | 0.05 | 0.923 | 20.5 | 0.8 | 0.09 | 13.8 | 1 | 1 | 0.08828 | 225 | 175 | 175 | 225 | 10.5 | 13.2 | 1 | -1 | 208-230/1/60 | 29 | 145 | 36.3 | 60 | -3 | 208-230/3/60 | 18 | 123 | 22.5 | 40 | -4 | 460/3/60 | 9.7 | 70 | 12.2 | 20 | 85 | 55 | 70 | 70 | Refrigerant R-410A |  | 1 | 17
16 | WW072 | 37824.9515 | 639.3589 | 29.534 | 8.9901 | 2.2592 | -1.521 | 0.057573 | -0.066196 | -0.0065349 | -0.000912 | -1525.209 | 4.7692 | 92.5911 | 0.079729 | -0.12881 | -0.73654 | -0.0002 | -0.0010289 | 0.000283 | 0.0036555 | 0.05 | 0.941 | 16.2 | 0.8 | 0.04 | 10.5 | 1.04 | 1.015 | 0.07828 | 250 | 200 | 200 | 250 | 11 | 13.7 | 1 | -1 | 208-230/1/60 | 28.8 | 169 | 36 | 60 | -3 | 208-230/3/60 | 19.3 | 129 | 24.2 | 40 | -4 | 460/3/60 | 9.7 | 75 | 12.2 | 20 | 85 | 55 | 70 | 70 | Refrigerant R-410A |  | 1 | 17
17 | WW120 | 104636.5893 | 288.1249 | -93.5177 | 6.2898 | 30.8532 | -6.699 | 0.0032031 | 0.061227 | -0.18672 | 0.027939 | 9611.2699 | 34.608 | -142.5014 | -0.88422 | 0.32175 | 1.1714 | -0.0024219 | 0.011523 | -0.0070394 | 0.000491 | 0.05 | 0.97 | 14 | 0.82 | 0.04 | 13.5 | 1.021 | 1 | 0.0277 | 350 | 300 | 300 | 350 | 22 | 28 | 1 | -3 | 208-230/3/60 | 37 | 239 | 46.3 | 80 | -4 | 460/3/60 | 20 | 125 | 25 | 40 | -5 | 575/3/60 | 14.3 | 80 | 17.9 | 30 | 85 | 55 | 70 | 70 | Refrigerant R-410A |  | 2 | 35
18 | WW122 | 37824.9515 | 639.3589 | 29.534 | 8.9901 | 2.2592 | -1.521 | 0.057573 | -0.066196 | -0.0065349 | -0.000912 | -1525.209 | 4.7692 | 92.5911 | 0.079729 | -0.12881 | -0.73654 | -0.0002 | -0.0010289 | 0.000283 | 0.0036555 | 0.05 | 0.95 | 17.3 | 0.86 | 0.04 | 7 | 1.92 | 2.05 | 0.0277 | 250 | 200 | 200 | 250 | 23 | 30 | 2 | -1 | 208-230/1/60 | 28.8 | 169 | 64.8 | 80 | -3 | 208-230/3/60 | 19.3 | 129 | 43.5 | 60 | -4 | 460/3/60 | 9.7 | 75 | 21.8 | 30 | 85 | 55 | 70 | 70 | Refrigerant R-410A |  | 2 | 35
19 | WW180 | 124509.6257 | 2315.2455 | -835.1083 | 25.8049 | -11.2176 | 5.2528 | 0.074805 | -0.15421 | 0.043099 | -0.026168 | 2082.1626 | 14.4293 | 53.152 | 0.016518 | 0.01222 | -0.22898 | 0.0012784 | 0.000273 | -0.0014292 | 0.0033888 | 0.05 | 0.97 | 13.5 | 0.8 | 0.04 | 11.5 | 1 | 1 | 0.0165 | 450 | 400 | 400 | 450 | 27 | 34 | 1 | -3 | 208-230/3/60 | 53.6 | 245 | 67 | 120 | -4 | 460/3/60 | 20.7 | 125 | 25.9 | 40 | -5 | 575/3/60 | 16.4 | 100 | 20.5 | 35 | 85 | 55 | 70 | 70 | Refrigerant R-410A |  | 2 | 50
20 | WW210 | 146844.7802 | 2530.0897 | -725.6045 | 28.1275 | -0.55501 | 1.8584 | 0.09198 | -0.11264 | -0.043758 | -0.0076663 | 5909.2372 | 159.8744 | -43.501 | 2.2867 | -3.8022 | 1.1543 | 0.014723 | -0.029084 | 0.022894 | -0.0019807 | 0.05 | 0.97 | 14.5 | 0.85 | 0.02 | 12 | 1.017 | 1.02 | 0.0165 | 400 | 325 | 325 | 400 | 32 | 40 | 1 | -3 | 208-230/3/60 | 59.1 | 425 | 73.9 | 130 | -4 | 460/3/60 | 26.4 | 187 | 33 | 50 | -5 | 575/3/60 | 26 | 148 | 32.5 | 50 | 85 | 55 | 70 | 70 | Refrigerant R-410A |  | 2 | 50
21 | WW240 | 104636.5893 | 288.1249 | -93.5177 | 6.2898 | 30.8532 | -6.699 | 0.0032031 | 0.061227 | -0.18672 | 0.027939 | 9611.2699 | 34.608 | -142.5014 | -0.88422 | 0.32175 | 1.1714 | -0.0024219 | 0.011523 | -0.0070394 | 0.000491 | 0.05 | 0.97 | 14 | 0.82 | 0.04 | 13.5 | 2.042 | 2 | 0.007955 | 700 | 600 | 600 | 700 | 44 | 56 | 2 | -3 | 208-230/3/60 | 37 | 239 | 83.3 | 120 | -4 | 460/3/60 | 20 | 125 | 45 | 60 | -5 | 575/3/60 | 14.3 | 80 | 32.2 | 45 | 85 | 55 | 70 | 70 | Refrigerant R-410A |  | 2 | 72
22 | WW360 | 124509.6257 | 2315.2455 | -835.1083 | 25.8049 | -11.2176 | 5.2528 | 0.074805 | -0.15421 | 0.043099 | -0.026168 | 2082.1626 | 14.4293 | 53.152 | 0.016518 | 0.01222 | -0.22898 | 0.0012784 | 0.000273 | -0.0014292 | 0.0033888 | 0.05 | 0.97 | 13.5 | 0.8 | 0.04 | 11.5 | 2 | 2 | 0.004738 | 900 | 800 | 800 | 900 | 54 | 68 | 2 | -3 | 208-230/3/60 | 53.6 | 245 | 120.6 | 170 | -4 | 460/3/60 | 20.7 | 125 | 46.6 | 60 | -5 | 575/3/60 | 16.4 | 100 | 36.9 | 50 | 85 | 55 | 70 | 70 | Refrigerant R-410A |  | 2 | 90
23 | WW420 | 146844.7802 | 2530.0897 | -725.6045 | 28.1275 | -0.55501 | 1.8584 | 0.09198 | -0.11264 | -0.043758 | -0.0076663 | 5909.2372 | 159.8744 | -43.501 | 2.2867 | -3.8022 | 1.1543 | 0.014723 | -0.029084 | 0.022894 | -0.0019807 | 0.05 | 0.97 | 14.5 | 0.85 | 0.02 | 12 | 2.034 | 2.04 | 0.004738 | 800 | 650 | 650 | 800 | 64 | 80 | 2 | -3 | 208-230/3/60 | 59.1 | 425 | 133 | 190 | -4 | 460/3/60 | 26.4 | 187 | 59.4 | 80 | -5 | 575/3/60 | 26 | 148 | 58.5 | 80 | 85 | 55 | 70 | 70 | Refrigerant R-410A |  | 2 | 90
Key | Error Codes - Cooling | [8 empty] | Key | Refrigerants
0 | [9 empty] | 1 | Refrigerant R-22
1 | Cooling - Low Leaving Load Temperature - add or increase antifreeze %. | [8 empty] | 2 | Refrigerant R-410A
10 | Cooling - Leaving Source Temperature Too High
100 | Cooling - Source Flow Rate Too Low
1000 | Cooling - Source Flow Rate Too High | [56 empty] | gpm | dia | area | velocity
10000 | Cooling - Load Flow Rate Too Low | [56 empty] | 17 | 1 | 0.7854 | 6.9437
100000 | Cooling - Load Flow Rate Too High | [55 empty] | 2 | 17 | 1 | 1.5708 | 3.4719
1000000 | Cooling - Head Pressure Too High | [55 empty] | 3 | 17 | 1 | 2.3562 | 2.3146
10000000 | Cooling - Suction Pressure Too Low | [55 empty] | 4 | 17 | 1 | 3.1416 | 1.7359
100000000 | Cooling - Suction Temperature Too High | [55 empty] | 5 | 17 | 1 | 3.927 | 1.3887
1000000000 | Cooling - Condensing Temperature Too Low | [55 empty] | 6 | 17 | 1 | 4.7124 | 1.1573
10000000000 | Cooling - Low Refrigerant Mass Flow - Head Press. Too High and/or Suction Press. Too Low
Error Codes - Heating
0
1 | Heating - Low Leaving Source Temperature - add or increase antifreeze %.
10 | Heating - Leaving Load Temperature Too High
100 | Heating - Source Flow Rate Too Low
1000 | Heating - Source Flow Rate Too High
10000 | Heating - Load Flow Rate Too Low
100000 | Heating - Load Flow Rate Too High
1000000 | Heating - Head Pressure Too High
10000000 | Heating - Suction Pressure Too Low
100000000 | Heating - Suction Temperature Too High
1000000000 | Heating - Condensing Temperature Too Low
10000000000 | Heating - Low Refrigerant Mass Flow - Head Press. Too High and/or Suction Press. Too Low
Selected Data For Calculations
Sort | Unit | Compressor Capacity Coefficients | [9 empty] | Compressor Watt Coefficients | [9 empty] | Condensing Temp Constants |  |  | Evaporating Temp Constants |  |  | Performance Modifiers |  | Delta P | Iteration 0 Values |  |  |  | Rated Flow | [20 empty] | Cooling |  | Heating
Key | Model | c0 | c1 | c2 | c3 | c4 | c5 | c6 | c7 | c8 | c9 | w0 | w1 | w2 | w3 | w4 | w5 | w6 | w7 | w8 | w9 | Evap | Cond | Approach | Evap | Cond | Approach | Capacity | Watts | Constant | LST (Clg) | LLT (Clg) | LST (Htg) | LLT (Clg) | Load | Source | Circuits | V-Code | Voltage | RLA | LRA | MCA | MFS | V-Code | Voltage | RLA | LRA | MCA | MFS | V-Code | Voltage | RLA | LRA | MCA | MFS | EST | ELT | EST | ELT | Refrigerant | Drawing | Max Flow
1 | WW024 | 14963.9639 | 324.799 | 32.3902 | 3.47 | 0.80192 | -1.0738 | 0.0080317 | -0.0062237 | -0.013859 | 0.0034513 | -962.2907 | -1.0012 | 48.6434 | 0.09544 | -0.086653 | -0.36396 | 0.0015494 | -0.0024703 | 0.0012234 | 0.0014217 | 0.05 | 0.99 | 12.8 | 0.8 | 0.08 | 8 | 0.96 | 1.05 | 0.174 | 100 | 75 | 75 | 100 | 5 | 6.2 | 1 | -1 | 208-230/1/60 | 13.5 | 61 | 16.9 | 30 | -3 | 208-230/3/60 | 8.3 | 63 | 10.4 | 15 | -4 | 460/3/60 | 5 | 27 | 6.3 | 15 | 85 | 55 | 70 | 70 | Refrigerant R-410A | 1 | 10
2 | WW036 | 20434.3789 | 408.4368 | -103.2717 | 4.6543 | -0.96454 | 0.46079 | 0.012 | -0.018883 | -0.0018459 | -0.0027202 | -427.9745 | -14.2724 | 41.4046 | -0.115 | 0.31743 | -0.37711 | 0.0007 | 0.000465 | -0.0017833 | 0.0019242 | 0.05 | 0.98 | 12.4 | 0.8 | 0.055 | 10 | 1.02 | 1 | 0.174 | 100 | 75 | 75 | 100 | 5.3 | 6.6 | 1 | -1 | 208-230/1/60 | 14.8 | 72.5 | 18.5 | 30 | -3 | 208-230/3/60 | 9.9 | 35 | 12.4 | 20 | -4 | 460/3/60 | 4.5 | 31 | 5.7 | 15 | 85 | 55 | 70 | 70 | Refrigerant R-410A | 1 | 12
3 | WW048 | 25244.5977 | 613.9734 | 45.4917 | 6.5826 | -0.7653 | -1.2072 | 0.015862 | -0.024127 | -0.0068058 | 0.0017693 | -1371.0541 | -31.1564 | 85.6462 | -0.37677 | 0.72406 | -0.80042 | -0.0013903 | 0.0040539 | -0.0044038 | 0.0036982 | 0.05 | 0.941 | 17.6 | 0.8 | 0.04 | 10.8 | 1.04 | 1.01 | 0.11643 | 175 | 125 | 125 | 175 | 8.1 | 10.1 | 1 | -1 | 208-230/1/60 | 20.6 | 109 | 25.8 | 45 | -3 | 208-230/3/60 | 14.1 | 91 | 17.7 | 30 | -4 | 460/3/60 | 7.1 | 46 | 8.9 | 15 | 85 | 55 | 70 | 70 | Refrigerant R-410A | 1 | 17
4 | WW060 | 36005.2461 | 907.9749 | -18.4169 | 9.6422 | -2.1577 | -0.99203 | 0.04578 | -0.06338 | 0.0017438 | 0.000452 | -2319.134 | -7.4615 | 112.0605 | -0.09131 | 0.11179 | -0.8882 | 0.0017189 | -0.000738 | -0.000364 | 0.0037419 | 0.05 | 0.923 | 20.5 | 0.8 | 0.09 | 13.8 | 1 | 1 | 0.08828 | 225 | 175 | 175 | 225 | 10.5 | 13.2 | 1 | -1 | 208-230/1/60 | 29 | 145 | 36.3 | 60 | -3 | 208-230/3/60 | 18 | 123 | 22.5 | 40 | -4 | 460/3/60 | 9.7 | 70 | 12.2 | 20 | 85 | 55 | 70 | 70 | Refrigerant R-410A | 1 | 17
5 | WW072 | 37824.9515 | 639.3589 | 29.534 | 8.9901 | 2.2592 | -1.521 | 0.057573 | -0.066196 | -0.0065349 | -0.000912 | -1525.209 | 4.7692 | 92.5911 | 0.079729 | -0.12881 | -0.73654 | -0.0002 | -0.0010289 | 0.000283 | 0.0036555 | 0.05 | 0.941 | 16.2 | 0.8 | 0.04 | 10.5 | 1.04 | 1.015 | 0.07828 | 250 | 200 | 200 | 250 | 11 | 13.7 | 1 | -1 | 208-230/1/60 | 28.8 | 169 | 36 | 60 | -3 | 208-230/3/60 | 19.3 | 129 | 24.2 | 40 | -4 | 460/3/60 | 9.7 | 75 | 12.2 | 20 | 85 | 55 | 70 | 70 | Refrigerant R-410A | 1 | 17
6 | WW120 | 104636.5893 | 288.1249 | -93.5177 | 6.2898 | 30.8532 | -6.699 | 0.0032031 | 0.061227 | -0.18672 | 0.027939 | 9611.2699 | 34.608 | -142.5014 | -0.88422 | 0.32175 | 1.1714 | -0.0024219 | 0.011523 | -0.0070394 | 0.000491 | 0.05 | 0.97 | 14 | 0.82 | 0.04 | 13.5 | 1.021 | 1 | 0.0277 | 350 | 300 | 300 | 350 | 22 | 28 | 1 | -3 | 208-230/3/60 | 37 | 239 | 46.3 | 80 | -4 | 460/3/60 | 20 | 125 | 25 | 40 | -5 | 575/3/60 | 14.3 | 80 | 17.9 | 30 | 85 | 55 | 70 | 70 | Refrigerant R-410A | 2 | 35
7 | WW122 | 37824.9515 | 639.3589 | 29.534 | 8.9901 | 2.2592 | -1.521 | 0.057573 | -0.066196 | -0.0065349 | -0.000912 | -1525.209 | 4.7692 | 92.5911 | 0.079729 | -0.12881 | -0.73654 | -0.0002 | -0.0010289 | 0.000283 | 0.0036555 | 0.05 | 0.95 | 17.3 | 0.86 | 0.04 | 7 | 1.92 | 2.05 | 0.0277 | 250 | 200 | 200 | 250 | 23 | 30 | 2 | -1 | 208-230/1/60 | 28.8 | 169 | 64.8 | 80 | -3 | 208-230/3/60 | 19.3 | 129 | 43.5 | 60 | -4 | 460/3/60 | 9.7 | 75 | 21.8 | 30 | 85 | 55 | 70 | 70 | Refrigerant R-410A | 2 | 35
8 | WW180 | 124509.6257 | 2315.2455 | -835.1083 | 25.8049 | -11.2176 | 5.2528 | 0.074805 | -0.15421 | 0.043099 | -0.026168 | 2082.1626 | 14.4293 | 53.152 | 0.016518 | 0.01222 | -0.22898 | 0.0012784 | 0.000273 | -0.0014292 | 0.0033888 | 0.05 | 0.97 | 13.5 | 0.8 | 0.04 | 11.5 | 1 | 1 | 0.0165 | 450 | 400 | 400 | 450 | 27 | 34 | 1 | -3 | 208-230/3/60 | 53.6 | 245 | 67 | 120 | -4 | 460/3/60 | 20.7 | 125 | 25.9 | 40 | -5 | 575/3/60 | 16.4 | 100 | 20.5 | 35 | 85 | 55 | 70 | 70 | Refrigerant R-410A | 2 | 50
9 | WW210 | 146844.7802 | 2530.0897 | -725.6045 | 28.1275 | -0.55501 | 1.8584 | 0.09198 | -0.11264 | -0.043758 | -0.0076663 | 5909.2372 | 159.8744 | -43.501 | 2.2867 | -3.8022 | 1.1543 | 0.014723 | -0.029084 | 0.022894 | -0.0019807 | 0.05 | 0.97 | 14.5 | 0.85 | 0.02 | 12 | 1.017 | 1.02 | 0.0165 | 400 | 325 | 325 | 400 | 32 | 40 | 1 | -3 | 208-230/3/60 | 59.1 | 425 | 73.9 | 130 | -4 | 460/3/60 | 26.4 | 187 | 33 | 50 | -5 | 575/3/60 | 26 | 148 | 32.5 | 50 | 85 | 55 | 70 | 70 | Refrigerant R-410A | 2 | 50
10 | WW240 | 104636.5893 | 288.1249 | -93.5177 | 6.2898 | 30.8532 | -6.699 | 0.0032031 | 0.061227 | -0.18672 | 0.027939 | 9611.2699 | 34.608 | -142.5014 | -0.88422 | 0.32175 | 1.1714 | -0.0024219 | 0.011523 | -0.0070394 | 0.000491 | 0.05 | 0.97 | 14 | 0.82 | 0.04 | 13.5 | 2.042 | 2 | 0.007955 | 700 | 600 | 600 | 700 | 44 | 56 | 2 | -3 | 208-230/3/60 | 37 | 239 | 83.3 | 120 | -4 | 460/3/60 | 20 | 125 | 45 | 60 | -5 | 575/3/60 | 14.3 | 80 | 32.2 | 45 | 85 | 55 | 70 | 70 | Refrigerant R-410A | 2 | 72
11 | WW360 | 124509.6257 | 2315.2455 | -835.1083 | 25.8049 | -11.2176 | 5.2528 | 0.074805 | -0.15421 | 0.043099 | -0.026168 | 2082.1626 | 14.4293 | 53.152 | 0.016518 | 0.01222 | -0.22898 | 0.0012784 | 0.000273 | -0.0014292 | 0.0033888 | 0.05 | 0.97 | 13.5 | 0.8 | 0.04 | 11.5 | 2 | 2 | 0.004738 | 900 | 800 | 800 | 900 | 54 | 68 | 2 | -3 | 208-230/3/60 | 53.6 | 245 | 120.6 | 170 | -4 | 460/3/60 | 20.7 | 125 | 46.6 | 60 | -5 | 575/3/60 | 16.4 | 100 | 36.9 | 50 | 85 | 55 | 70 | 70 | Refrigerant R-410A | 2 | 90
12 | WW420 | 146844.7802 | 2530.0897 | -725.6045 | 28.1275 | -0.55501 | 1.8584 | 0.09198 | -0.11264 | -0.043758 | -0.0076663 | 5909.2372 | 159.8744 | -43.501 | 2.2867 | -3.8022 | 1.1543 | 0.014723 | -0.029084 | 0.022894 | -0.0019807 | 0.05 | 0.97 | 14.5 | 0.85 | 0.02 | 12 | 2.034 | 2.04 | 0.004738 | 800 | 650 | 650 | 800 | 64 | 80 | 2 | -3 | 208-230/3/60 | 59.1 | 425 | 133 | 190 | -4 | 460/3/60 | 26.4 | 187 | 59.4 | 80 | -5 | 575/3/60 | 26 | 148 | 58.5 | 80 | 85 | 55 | 70 | 70 | Refrigerant R-410A | 2 | 90